PRODUCT SPECIFICATION

    AEROFLEX Closed Cell Elastomeric Thermal Insulations

| PHYSICAL PROPERTIES  |  | AEROFLEX |  |  |  | TEST METHOD |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cell Structure |  | Closed Cell |  |  |  | - |  |
| Density Ibs/ft3(kg/m3) |  | 3-6 (48-96)  |  |  |  | ASTM D 1667 |  |
| Thermal Conductivity BTU.in/ft2 hr. F (W/mk) | Mean Temp. | -4 F (-20 C) | 32 F (0 C) | 75 F (24 C) | 90 F (32 C) | 104 F (40 C) | ASTM C 518, C 177 JIS A 1412 DIN 52613 |
|  | K-value | 0.22 0.032 | 0.23 0.034 | 0.25 0.037 | 0.26 0.038 | 0.27 0.039 |  |
| Service temperature  |  | -70 F to 257 F -57 C - + 125 C |  |  |  | AEROFLEX becomes Hard at -57 C, but Can be used even at -200C |  |
| Water Vapor permeability (g/Pa.s.m) |  | 0.10 perm-in (1.44x10-10) |  |  |  | ASTM E96 |  |
| Moisture Resistance (µ value) |  | µ 7000 |  |  |  | DIN 52615 |  |
| Water Absorption (% by weight) |  |  5 |  |  |  | ASTM D 1056 |  |
| Ozone Resistance |  | No crack |  |  |  | ASTM D 1171, D 1149 |  |
| Heat Stability (% shrinkage) 200 F (93 C) 7 days |  | 6 |  |  |  | ASTM C 534 |  |
| Flammability & smoke, Density |  | Class V O |  |  |  | UL – 94 |  |
|  |  | 25/50 |  |  |  | ASTM E 84 |  |
|  |  | Self – extinguishing |  |  |  | ASTM E 635 |  |
|  |  | Class 5.3 |  |  |  | EMPA (Switzerland) |  |
|  |  | Non-Flammable |  |  |  | JIS K 6911 |  |
|  |  | Pass |  |  |  | IMO  |  |
| U.V. Weather Resistance |  | Excellent |  |  |  | - |  |
| Corrosion of copper, stainless |  | Non corrosive |  |  |  | DIN 1988 |  |
| Nitrosamine Contents |  | Not Detected |  |  |  | U.S. FDA |  |
| Sound reduction (LAF) |  | 27 dB (20 mm) |  |  |  | DIN 52218 |  |
| Flexibility |  | Excellent |  |  |  | - |  |

Specifications Company ASTM C534

Figures show the average values obtained by the world well-known testing institutes

 Tested according to DIN, JISASTM and others.

Average density of insulation thickness  20mm is 2.5 – 5 Ibs/ft3 (40 – 80 kg/m3)

At temp. under -57 CAEROFLEX become hard, but it doesn’t affect thermal conductivity nor  water vapor permeability.

In the heating applications AEROFLEX can Stan + 125 C   continuously, and the adhesive upto +100 C

IMO : International Martime Organization, IMO fire test procedures code part 5 and part 2  [IMO res. A.653[16]]

- Lioyd’s type approval certificate

- DNY’s type approval certificate

It is reported that Nitrosamine is harmful to human health even during storage. No Nitrosamine compound was

detected in AEROFLEX

| Properties | Aeroflex-Standard | Test Method |
| --- | --- | --- |
| Mold Resistance | Meet Requirement (Rating 1) | UL 181 |
| Fungi Resistance | No Growth | ASTM C1338 |
| Bacteria Resistance | Meet Requirement (Anti-Bacteria) | ASTM E 2180 |
| Corrosion of Copper/Stainless Steel | Non Corrosive | DIN 1988 |
| Nitrosamine Contents | Not Detected | FDA CPG 7117.11 |
| RoHS | Not Detected | EN Restriction of the Use of Hazardous Substances Directive (RoHS) 2002/95/EC |
| Sound Reduction (AF) | 32 dB(20 mm) | DIN EN ISO10052, DIN 4109-11 |
| Flexibility | Excellent | ASTM C 534 |